## SandBed_DesignOccupancy
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
Occupancy | Design Occupancy
Treatment system | AES Recirculation
Treatment level | Advanced secondary treatment with recirculation (500%) |  |  | 1 | Table number
Land application system | Sand bed (600mm)
Land area | 5000 | m2
Table 1: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 7 | persons | Maximum design occupancy
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 1400 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 30.66 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 87% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 7.8 | mg/L | OSET NTP Trial 13 - AES-R discharge mean N concentration
Total N reduction in sand column | 25% |  | EPA2, Converse, Crites3
Total N concentration after sand column | 5.85 | mg/L
Total N reduction over untreated effluent | 90.25% |  | Calculated N reduction
Total N load exiting sand trench | 2.9894 | kg/yr | 5.85 mg/L * 1400 L/day *365 days/year
Total N exiting sand trench | 5.9787 | kg/ha/yr | Over the total land area of 5000m2
N concentration below LAS | 5.85 | mg/L | Calculated N concentration ignoring rainfall
Calculation of N reduction below land application system
Total N reduction by denitrification | 0% |  | No reduction modelled |  |  | Gardner et al 19974
N concentration at groundwater | 5.85 | mg/L
Total N load to groundwater | 2.9894 | kg/yr | 5.85 mg/L * 1400 L/day *365 days/year
| 5.9787 | kg/ha/yr | Over the total land area of 5000m2 |  |  | 1071.4286
Notes:
(1) OSET Trials
(2) US EPA (2002) suggests 18 -33% TN reduction for primary treated effluent in a sand bed, Converse suggests 40%.
(3) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 25% has been used in this assessment
(4) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (5) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408

## SandBed_AverageOccupancy
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
Occupancy | Average Occupancy
Treatment system | Oasis Series 2000
Treatment level | Standard treatment |  |  | 4 | Table number
Land application system | Sand bed (600mm)
Land area | 5000 | m2
Table 4: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 2.6 | persons | Maximum design occupancy |  | Statistics NZ data shows average occupancy for Ashburton is 2.6 people per house
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 520 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 11.388 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 65% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 21 | mg/L | OSET NTP Trial 10 - Oasis Series 2000 mean concentration (1)
Total N reduction in sand column | 35% |  | Ref: Crites et al 1998, Table 11-13, p 743 (2)
Total N concentration after sand column | 13.65 | mg/L
Total N reduction over untreated effluent | 77.25% |  | Calculated N reduction
Total N load exiting sand trench | 2.5908 | kg/yr | 13.65 mg/L * 520 L/day *365 days/year
Total N exiting sand trench | 5.1815 | kg/ha/yr | Over the total land area of 5000m2
N concentration below LAS | 13.65 | mg/L | Calculated N concentration ignoring rainfall
Calculation of N reduction below land application system
Total N reduction by denitrification | 20% |  | Gardner et al 19973
N concentration at groundwater | 10.92 | mg/L
Total N load to groundwater | 2.0726 | kg/yr | 10.92 mg/L * 520 L/day *365 days/year
| 4.1452 | kg/ha/yr | Over the total land area of 5000m2
Notes:
(1) OSET Trials
(2) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 35% has been used in this assessment
(3) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (4) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408

## SandBed_DesignOccupancyAES_X5
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
Occupancy | Design Occupancy
Treatment system | AES with recirculating sandbed
Treatment level | 500% recirculation for addition N removal |  |  | 2 | Table number
Land application system | Sand bed (600mm)
Land area | 5000 | m2
Table 2: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 7 | persons | Maximum design occupancy
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 1400 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 30.66 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 87% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 7.8 | mg/L | OSET NTP Trial 13 - AES 2000 mean concentration (1)
Total N reduction in sand column | 35% |  | Ref: Crites et al 1998, Table 11-13, p 743 (2)
Total N concentration after sand column | 5.07 | mg/L
Total N reduction over untreated effluent | 91.55% |  | Calculated N reduction
Total N load exiting sand trench | 2.5908 | kg/yr | 5.07 mg/L * 1400 L/day *365 days/year
Total N exiting sand trench | 5.1815 | kg/ha/yr | Over the total land area of 5000m2
N concentration below LAS | 5.07 | mg/L | Calculated N concentration ignoring rainfall
Calculation of N reduction below land application system
Total N reduction by denitrification | 20% |  | Gardner et al 19973
N concentration at groundwater | 4.056 | mg/L
Total N load to groundwater | 2.0726 | kg/yr | 4.056 mg/L * 1400 L/day *365 days/year
| 4.1452 | kg/ha/yr | Over the total land area of 5000m2
Notes:
(1) OSET Trials
(2) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 35% has been used in this assessment
(3) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (4) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408