## AverageOccupancy
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
|  |  |  | 2 | Table number
Occupancy | Average Occupancy
Treatment system | Oasis Series 2000
Treatment level | Standard treatment
Land application system | Dripline
Land application system area | 350 | m2
Total land area | 5000 | m2
Table 2: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 2.6 | persons | Maximum design occupancy |  | Statistics NZ data shows average occupancy for Ashburton is 2.6 people per house
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 520 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 11.388 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 65% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 21 | mg/L | OSET NTP Trial 10 - Oasis Series 2000 mean concentration (1)
Total N load exiting Dripline | 3.9858 | kg/yr | 21 mg/L * 520 L/day *365 days/year | ok
| 113.88 | kg/ha/yr | Over the LAS land area of 350m2
Calculation of N reduction below Dripline land application system
Total N reduction by denitrification | 20% |  | Gardner et al 19973 | Oasis testing at Synlait couldn't detect N at 200mm below the dripline - pers comm Graham at Oasis
| 22.776 | kg/ha/yr | N removed by denitrification under LAS
N reduction through plant uptake | 60 | kg/ha/yr | Wheeler, Edmeades, Morton 19964 | Assume 60 kg based on low N load, could be up to 200kg
Total N load to groundwater | 31.104 | kg/ha/yr | Over the LAS land area of 350m2
| 1.0886 | kg/yr
Total N concentration at groundwater | 5.7357 | mg/L | N leached to groundwater / volume of effluent
Notes:
(1) OSET Trials
(2) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 2100% has been used in this assessment
(3) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (4) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408

## DesignOccupancy
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
|  |  |  | 3 | Table number
Occupancy | Maximum design occupancy
Treatment system | Oasis Series 2000
Treatment level | Standard treatment
Land application system | Dripline
Land application system area | 350 | m2
Total land area | 5000 | m2
Table 3: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 7 | persons | Maximum design occupancy
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 1400 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 30.66 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 65% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 21 | mg/L | OSET NTP Trial 10 - Oasis Series 2000 mean concentration (1)
Total N load exiting Dripline | 10.731 | kg/yr | 21 mg/L * 1400 L/day *365 days/year | ok
| 306.6 | kg/ha/yr | Over the LAS land area of 350m2
Calculation of N reduction below Dripline land application system
Total N reduction by denitrification | 20% |  | Gardner et al 19973 | Oasis testing at Synlait couldn't detect N at 200mm below the dripline - pers comm Graham at Oasis
| 61.32 | kg/ha/yr | N removed by denitrification under LAS
N reduction through plant uptake | 150 | kg/ha/yr | Wheeler, Edmeades, Morton 19964 | Assume 150 kg, could be up to 200kg
Total N load to groundwater | 95.28 | kg/ha/yr | Over the LAS land area of 350m2
| 3.3348 | kg/yr
Total N concentration at groundwater | 6.526 | mg/L | N leached to groundwater / volume of effluent
Notes:
(1) OSET Trials
(2) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 2100% has been used in this assessment
(3) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (4) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408

## DesignOccupancy_AESx5
Nitrogen discharge to land
Marriott - Haugh
46 McGrath Road, Ashburton |  |  |  |  | Cells for data entry
|  |  |  | 5 | Table number
Occupancy | Design
Treatment system | AES with recirculating sandbed
Treatment level | 500% recirculation for addition N removal
Land application system | Dripline
Land application system area | 500 | m2
Total land area | 5000 | m2
Table 5: Total Nitrogen Assessment
Calculation of Total N in the Domestic Effluent
Daily occupancy | 7 | persons | Maximum design occupancy
Daily volume | 200 | L/person/day | Environment Canterbury - no reeduction fixtures
| 1400 | L/day
Days occupancy/year | 365 | days
Total N Concentration of influent | 60 | mg/L | Average concentration from AS/NZS 1547:2012, Table S1
Total N in wastewater | 12 | g/person/day
| 4.38 | kg/person/year
| 30.66 | kg/house/year
Calculation of N reduction in treatment system
Total N reduction in treatment plant | 87% |  | Calculation to achieve OSET average N concentration
Total N concentration after treatment plant | 7.8 | mg/L | OSET NTP Trial 13 - AES 2000 mean concentration (1)
Total N load exiting Dripline | 3.9858 | kg/yr | 7.8 mg/L * 1400 L/day *365 days/year
| 79.716 | kg/ha/yr | Over the LAS land area of 500m2
Calculation of N reduction below Dripline land application system
Total N reduction by denitrification | 20% |  | Gardner et al 19973 | Oasis testing at Synlait couldn't detect N at 200mm below the dripline - pers comm Graham at Oasis
| 15.9432 | kg/ha/yr | N removed by denitrification under LAS
N reduction through plant uptake | 50 | kg/ha/yr | Wheeler, Edmeades, Morton 19964 | Assume 50 kg, could be up to 200kg
Total N load to groundwater | 13.7728 | kg/ha/yr | Over the LAS land area of 500m2
| 0.68864 | kg/yr
Total N concentration at groundwater | 1.3476 | mg/L | N leached to groundwater / volume of effluent
Notes:
(1) OSET Trials
(2) Crites at al 1998 suggests 28 -50% TN reduction for secondary treated effluent in a sand bed. 780% has been used in this assessment
(3) Gardner et al 1997. Ecological Sustainability and On-Site Effluent Treatment Systems, Australian Jurnal of Environmental Management, 4: 144-156 (4) D. M. Wheeler, D. C. Edmeades & J. D. Morton (1997) Effect of lime on yield, N fixation, and plant N uptake from the soil by pasture on 3 contrasting trials in New Zealand, New Zealand Journal of Agricultural Research, 40:3, 397-408