## SandBed
Type of Discharge field | Sand bed
Area of discharge field | 28 | m2 | [5 empty] | Nitrogen concentration in groundwater after mixing
Treated wastewater N concentration | 15.4 | g/m3
Rainfall | 700 | mm/year | [5 empty] | Marriott-Haugh & Haugh
ET | 850 | mm/year | [5 empty] | 46 McGrath Road, Ashburton
DLR | 50 | mm/day
[8 empty] | Occupancy |  |  | Design Occupancy
Size of sand med - m2 | 32 | 28 | 24 | 20 | 16 | 12 | 8 | Design wastewater volume |  |  | 1600
Wastewater volume - L/day | 1600 | 1400 | 1200 | 1000 | 800 | 600 | 400 | Treatment system |  |  | AES - Recirculating
Wastewater volume - m3/year | 584 | 511 | 438 | 365 | 292 | 219 | 146 | Treatment level |  |  | Advanced secondary treatment
Wastewater volume - m3/year/m2 | 20.8571 | 18.25 | 15.6429 | 13.0357 | 10.4286 | 7.8214 | 5.2143 | Land application system |  |  | Sand bed (600mm)
plus | [7 empty] | Land area |  |  | 5000 | m2
Rainfall - m3/year | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 19.6
Rainfall - m3/year/m2 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Calculation of Nitrogen concentration in groundwater after mixing | [5 empty] | Calculation Co = (CiQn + CnQn)/(Qi + Qn) - Note 1
less
Evaotraspiration - m3/year | -23.8 | -23.8 | -23.8 | -23.8 | -23.8 | -23.8 | -23.8 | Concentration of N in groundwater |  |  | Cn | 15 | mg/L | Assumed
Evaotraspiration - m3/year/m2 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | Concentration of N in wastewater input |  |  | C1 | 5.9 | mg/L | N reduction calculation spreadsheet
Net rainfall | -4.2 | -4.2 | -4.2 | -4.2 | -4.2 | -4.2 | -4.2
Flow of groundwater
Total volume wastewater + rainfall - m3/year | 579.8 | 506.8 | 433.8 | 360.8 | 287.8 | 214.8 | 141.8 | Transmissivity |  |  |  | 4371.6538 |  | Geomean of aquifer tests in surrounding bores (see calculation)
Total volume wastewater + rainfall - m3/year/m2 | 20.7071 | 18.1 | 15.4929 | 12.8857 | 10.2786 | 7.6714 | 5.0643 | Aquifer depth |  |  |  | 10 | m
[8 empty] | Hydraulic conductivity (T/Depth) |  |  |  | 437.1654
Application volume - m3/year | [7 empty] | Mixing zone |  | (z) |  | 2 | m | Aquifer depth = 10 m, water level = 2 m, mixing zone = 8 m)
Application depth | 20.8571 | 18.25 | 15.6429 | 13.0357 | 10.4286 | 7.8214 | 5.2143 | Hydraulic gradient (i) |  |  |  | 0.0058708 |  | Piezometric contours
Plus net rainfall
less ET | [7 empty] | Qn |  |  |  | 1873.5659 | m3 | GW flow over year
Depth of
Flow of input (drainage)
[8 empty] | Length of LAS parallel to direction of GW flow |  |  |  | 1.8 | m
Nitrogen - kg/year | 8.9936 | 7.8694 | 6.7452 | 5.621 | 4.4968 | 3.3726 | 2.2484 | Additional drainage |  |  |  | 20.86 | m | Drainage from wastewater applied to LAS - see calculation
Nitrogen - kg/year/m2 | 0.3212 | 0.28105 | 0.2409 | 0.20075 | 0.1606 | 0.12045 | 0.0803
Nitrogen concentration at bottom of LAS - g/m3 | 15.5116 | 15.5276 | 15.5491 | 15.5793 | 15.6247 | 15.7011 | 15.8561 | Qi | (L * 1m * additional drainage) |  |  | 37.548 | m3 | Annual drainage through LAS
[8 empty] | N Concentration of groundwater after mixing |  |  |  | 14.8212 | mg/L | N concentration of drainage mixed with groundwater
[8 empty] | change in N concentration |  |  |  | -0.17879 | mg/L
Bores for Transmissivity
[8 empty] | L37/0720 | 41.2 | 9000
[8 empty] | L37/0030 | 38 | 8500
[8 empty] | L37/1171 | 30 | 1600
[8 empty] | L37/1430 | 50.79 | 3574
[8 empty] | BY21/0068 | 90 | 3650
[8 empty] | Geomean |  | 4371.6538
Note 1: Ecan document - GUIDELINES FOR DETERMINING SIGNIFICANCE OF ENVIRONMENTAL IMPACTS RESULTING FROM USE OF WATER FOR IRRIGATION

## DripLine
Type of Discharge field | Dripline
Area of discharge field | 350 | m2 | [5 empty] | Nitrogen concentration in groundwater after mixing
Treated wastewater N concentration | 15 | g/m3
Rainfall | 700 | mm/year | [5 empty] | Marriott - Haugh
ET | 850 | mm/year | [5 empty] | 46 McGrath Road, Ashburton
DLR | 4 | mm/day
[8 empty] | Occupancy |  |  | Design Occupancy
Size of sand med - m2 | 400 | 350 | 300 | 250 | 200 | 150 | 100 | Design wastewater volume |  |  | 1400 L/day
Wastewater volume - L/day | 1600 | 1400 | 1200 | 1000 | 800 | 600 | 400 | Treatment system |  |  | Oasis Series 2000 or similar
Wastewater volume - m3/year | 584 | 511 | 438 | 365 | 292 | 219 | 146 | Treatment level |  |  | Standard treatment
Wastewater volume - m3/year/m2 | 1.6686 | 1.46 | 1.2514 | 1.0429 | 0.83429 | 0.62571 | 0.41714 | Land application system |  |  | Dripline (300 m2)
plus | [7 empty] | Land area |  |  | 5000 | m2
Rainfall - m3/year | 245 | 245 | 245 | 245 | 245 | 245 | 245
Rainfall - m3/year/m2 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Calculation of Nitrogen concentration in groundwater after mixing | [5 empty] | Calculation Co = (CiQn + CnQn)/(Qi + Qn) - Note 1
less
Evaotraspiration - m3/year | -297.5 | -297.5 | -297.5 | -297.5 | -297.5 | -297.5 | -297.5 | Concentration of N in groundwater |  |  | Cn | 7.5 | mg/L
Evaotraspiration - m3/year/m2 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | -0.85 | Concentration of N in wastewater input |  |  | C1 | 6.5 | mg/L
Net rainfall | -52.5 | -52.5 | -52.5 | -52.5 | -52.5 | -52.5 | -52.5
Flow of groundwater
Total volume wastewater + rainfall - m3/year | 531.5 | 458.5 | 385.5 | 312.5 | 239.5 | 166.5 | 93.5 | Transmissivity |  |  |  | 4180 |  | Geomean of aquifer tests in surrounding bores (see calculation)
Total volume wastewater + rainfall - m3/year/m2 | 1.5186 | 1.31 | 1.1014 | 0.89286 | 0.68429 | 0.47571 | 0.26714 | Aquifer depth |  |  |  | 30 | m
[8 empty] | Hydraulic conductivity (T/10) |  |  |  | 139.3333
Application volume - m3/year | [7 empty] | Mixing zone |  | (z) |  | 15 | m | Aquifer depth = xm, water level = y m, mixing zone = z m)
Application depth | 1.6686 | 1.46 | 1.2514 | 1.0429 | 0.83429 | 0.62571 | 0.41714 | Hydraulic gradient (i) |  |  |  | 0.005 |  | Ashburton Rakaia 2010 bores <50m (20m/3905m)
Plus net rainfall
less ET | [7 empty] | Qn |  |  |  | 3814.25 | m3 | GW flow over year
Depth of
Flow of input (drainage)
[8 empty] | Length of LAS parallel to direction of GW flow |  |  |  | 5 | m
Nitrogen - kg/year | 8.76 | 7.665 | 6.57 | 5.475 | 4.38 | 3.285 | 2.19 | Additional drainage |  |  |  | 18.25 | m | Drainage from wastewater applied to LAS - see calculation
Nitrogen - kg/year/m2 | 0.025029 | 0.0219 | 0.018771 | 0.015643 | 0.012514 | 0.0093857 | 0.0062571
Nitrogen concentration at bottom of LAS - g/m3 | 16.4817 | 16.7176 | 17.0428 | 17.52 | 18.2881 | 19.7297 | 23.4225 | Qi | (L * 1m * additional drainage) |  |  | 91.25 | m3 | Annual drainage through LAS
[8 empty] | N Concentration of output |  |  |  | 7.4766 | mg/L | N concentration of drainage miced with groundwater
[8 empty] | change in N concentration |  |  |  | -0.023364 | mg/L
Bores for Transmissivity
[8 empty] | L37/0720 | 41.2 | 9000
[8 empty] | L37/0030 | 38.7 | 8500
[8 empty] | L37/1264 | 40.3 | 1800
[8 empty] | L37/1171 | 30 | 1600
[8 empty] | BY21/0376 | 33 | 5798
[8 empty] | Geomean |  | 4180.8677
Note 1: Ecan document - GUIDELINES FOR DETERMINING SIGNIFICANCE OF ENVIRONMENTAL IMPACTS RESULTING FROM USE OF WATER FOR IRRIGATION